## Slide 1: Phosphorus Extraction Technologies
WE Toffey 23 March 2020

## Slide 2: Shout Out to Tradition
Class B cake to farms: This is low cost, proven approach to phosphorus recycling
Class A biosolids-derived products: Compost and heat-dried pellets are marketable P-rich products for soil improvement and plant fertilization

## Slide 3: Challenge: Nutrient Balance
CNP AirPrex in Berlin
Ostara’s Pearl Process
Renewable Nutrients QuickWash
The balance of N and P in biosolids is agronomically wrong. The engineering challenge of the day is to extract phosphorus and to retain nitrogen in the biosolids. We are still waiting for the right combination of technologies…

## Slide 4: Drivers for P Extraction
Meet effluent discharge standards
Reduce struvite mineralization of equipment
Improve the dewaterability of Bio-P sludges (higher % solids, lower polymer usage)
Recover marketable P fertilizer
Improve N to P ratio in biosolids product
Achieve local and global sustainability goals

## Slide 5: Starting Point: How You Meet Effluent Discharge Standards
Enhanced Biological Phosphorus Removal
Phosphorus Accumulating Organisms (PAO) release extracellular polymeric substances (EPS) with highly soluble phosphorus under stress
EPS interferes with dewatering
Dewatering releases soluble P into filtrate/centrate
P in biosolids highly soluble and leachable
Chemical Phosphorus Removal
Use iron or aluminum salts to precipitate phosphorus as an insoluble mineral, incorporated into biosolids
Iron adds to biosolids mass, but aids dewaterability
Iron bound P will not solubilize and cannot be extracted from biosolids

## Slide 6: Ending Point: How You Use Biosolids Resources
Landfill disposal: Biosolids-borne P “lost to agriculture” forever
Agricultural land spreading: Biosolids-borne P can build up soil to high concentrations after repeated applications
Land restoration: Biosolids-borne P restores missing P
Incineration: Generally landfilled, but P value can be used.

## Slide 7: P Treatment Approaches
Controlled chemical precipitation to avoid struvite build up within treatment plant
  Sidestream precipitation as struvite after dewatering
  Precipitation of P mineral post digestion, but before dewatering
  Precipitation of P mineral pre-digestion.

## Slide 8: Distinction of Phosphorus Minerals
Brushite (dicalcium phosphate dihydrate or DCPD) forms in slightly acidic conditions of pH 4.5 – 6.5 and is a good fertilizer.
Ca2+ + H2PO4- + 2H2O CaHPO4·2H2O + H+
Struvite (magnesium ammonium phosphate) forms in slightly alkaline conditions of around pH 8 and is a good fertilizer.
NH4+ + Mg2+ + HPO42- + 6H2O  NH4MgPO4·6H2O + H+

## Slide 9: Ostara Technology: The Pearl® Reactor
TREATED EFFLUENT
RECYCLE LINE
MAGNESIUM
POST-DIGESTION DEWATERING LIQUOR + WASSTRIP® FEED
CRYSTAL GREEN
Notes: We have talked about Ostara’s recovery solution which is a combination of Pearl and Wasstrip.
This picture shows a schematic of what is happening in the pearl reactor. You have nutrient rich influent and wasstrip feed that comes into the bottom of the fluidized bed upflow reactor.
Chemicals are added to create ideal reaction conditions with supersaturated magnesium at the proper pH.
Reactor contents are recycled and treated effluent flows from the top of the reactor.
Periodically an operator will start a harvest cycle to harvest Crystal Green.

## Slide 10: Pearl® + WASSTRIP® Advanced Digestion Integration
High PO4 and NH3
High PO4 and Mg
WASSTRIP®
Mitigates struvite in digester
PEARL®
Recovers high value fertilizer and reduces recycle P load
THP
ANAEROBIC DIGESTION
THICKENING
ACTIVATED SLUDGE
SECONDARY CLARIFICATION
DEWATERING
DISCHARGE
INFLUENT
PRIMARY
DEWATERING
BIOSOLIDS
Notes: Biological nutrient removal efficiently and effectively reduces effluent nutrient concentration by using an aerobic and an anaerobic zone in the activated sludge process, this causes special bacteria called phosphorus accumulating organisms or PAOs to grow. These bugs take extra phosphorus into their cell walls in aerobic environments so that in the anaerobic zone they can use the P to consume VFAs (volatile fatty acids) in the anaerobic zone. This reduces the effluent phosphorus leaving the facility.
However when the waste activated sludge that his high in P, N, Mg, and K goes into the anaerobic digester, the P is released. This dissolved P is often returned to the head of the plant with the dewatering centrate or it can cause accidental struvite formation.

## Slide 11: CNP Pre and Post Digestion P Recovery

## Slide 12: CalPrex™ P Recovery
Fermentation P-Release
P- enriched Centrate
CalPrex Reactor
Brushite
CaHPO4 ·2H2O
P- reduced Centrate with high VFA
Methanogenic Digester
Carbon Supplement for Biological Nutrient Removal

## Slide 13: AirPrex® P-Recovery
Methane
Digester
Digested sludge with high PO4-P
Digested sludge with low PO4-P
Struvite
NH4MgPO4· 6H2O

## Slide 14: Schwing Bioset NuReSys
Three primary configurations: Hybrid
  Air Stripper has 2-hr HRT; Crystallizer has 1-hr HRT
  PO4-P levels down to ~15 ppm regardless of starting concentration
  Prevents scaling in upstream equipment AND centrate lines
  Harvest 90+% of struvite produced w/ optional cyclone
  Same lower MgCl2 dose as centrate option
  Can convert Digestate to Hybrid configuration in future
  Does not help dewatering performance as MgCl2 added downstream

## Slide 15: Conventional P Mass Balance
Final Effluent
10
Primary Sludge
10
Waste Activated Sludge
80
Anaerobic Digestion
90
Biosolids
85
Headworks / Recycle
<5
Wastewater Treatment Plant Influent
100
With no other exit, P mass is removed in biosolids through:
chemical sequestration
unintentional struvite formation
biomass accumulation

## Slide 16: P Balance with Side Stream Recovery
Final Effluent
10
Primary Sludge
10
Waste Activated Sludge
80
Anaerobic Digestion
90
Biosolids
75
Headworks / Recycle
<5
Wastewater Treatment Plant Influent
100
Side stream recovery converts approximately 15% percent of influent phosphorus into marketable P fertilizer product.
Phosphorus Recovery ~20

## Slide 17: P Balance with Combined System
Final Effluent
10
Primary Sludge
10
Waste Activated Sludge
80
WASSTRIP
80
Anaerobic Digestion
60
Crystal Green
40
Biosolids
45
Headworks
5
Wastewater Treatment Plant
100
Pearl
45
Converts Approximately 40% Of Influent Phosphorus Into Extracted Fertilizer Product

## Slide 18: P Mass Balance with CNP Pilot
Validation Criteria | Target Value | Average Field Value
Solubilization of P in Bio-P Sludge | at least 60% | 66%
Soluble P in CalPrex™ Reactor | 50-100 mg/L | 50 mg/L
Reduction of Total P in Biosolids | up to 50% | TBD*
*Averages of 8 mass balance samplings based on field testing by CNP engineers
65%
average recovery of ortho P that could otherwise precipitate as struvite downstream
87%
of the ortho-P entering the reactor was precipitated
92%
particulate capture rate in clarifier
43%
average recovery of total P from sludge feed

## Slide 19: Case Studies – Ostara
HRSD Nansemond Plant,
Madison, WI
Clean Water Services, OR
MWRD Greater Chicago Stickney Plant
Gwinnett County GA
Atlanta, GA
19 others in North America

## Slide 20: Case Studies – CNP AirPrex
Howard County DPA
Denver Metro
European Reference Facilities

## Slide 21: Case Studies – Schwing NuReSys
Tucson, AZ
Grand Rapids, MI

## Slide 22: Other Extraction Technologies
Renewable Nutrients – “Quick Wash”: Project development at stand-alone food digester in NE US and at WRRF in mid-West
Thermal Process Systems – “Targeted P Removal”: Pilot plant in Indiana
Absorbents -

## Slide 23: Renewable Nutrients Quick Wash
Using both P extraction and Nitrogen extraction approaches for digestate or filtrate, or combined treatment

## Slide 24: Thermal Process System
Enhanced Biological Nutrient Removal
Phosphorus uptake by bacteria
ATAD
Thermal hydrolysis
Phosphorus Release
VS & COD Destruction
Acid Phase Digester
Acid hydrolysis
Phosphorus Release
Denitrification
SGR
Nitrification
EPS Reduction
Alkalinity Reduction
Anaerobic Digester
VS & COD Destruction
SNDR
Nitrification/Denitrification
EPS Reduction
Alkalinity Reduction
TPR
Dewatering
Low P Return
Low P Return
TPR
Dewatering
Low P Cake P Product
Low P Cake P Product
Notes: Conditioning criteria present in the pilot systems

## Slide 25: Case Study – SSI Ash
German Policy Directive: example, TetraPhos from Remondis Aqua, wet chemical extraction of P from SSI Ash; also EasyMining Sweden, and Outotech GmbH.
Direct Use of SSI Ash for P fertilization: NEORSD Southerly, Cleveland, OH (Nick Basta, The Ohio State University); Metro Council Environmental Services, Minneapolis, MN (Persephone Ma, University of Minnesota)